# Tender text

# Motion detector theMura S180-101 B UP

Order No.: 			2060755

Features:

- Passive infrared presence detector for wall mounting in flush-mounted box

- Without cover, suitable for many common switch ranges (with accessories), for details see www.theben.de/theMura

- Automatic presence- and brightness-dependent control for lighting and HVAC

- Rectangular detection area 170°, max. 14 m x 17 m

- Area restriction in scope of delivery

- Mixed light measurement suitable for fluorescent lamps (FL/PL/ESL), halogen/incandescent lamps and LEDs

- Integrated button (can be deactivated)

- Connection option for external button

- Fully or semi-automatic operation, switchable

- Staircase light function

- Extended function

- Adjustable brightness switching value, teach-in function

- Reduction of time delay when present briefly (short-term presence)

- Pulse function for staircase light timer switch

- Configurable detection sensitivity

- Integrated orientation light

- Acoustic function

- Ready for immediate use due to factory presetting

- Can be configured remotely with remote control

- Test mode for checking the detection area

- Extension of detection area via master/slave switching

Technical data:

Operating voltage: 		      230 V AC

Frequency: 			      50 – 60 Hz

Power consumption: 		      approx. 0.4 W

Radial detection area: 		      12 x 10 m

Tangential detection area: 	      14 x 17 m

Installation height Mh: 		      0.8 – 1.2 m

Channel A Light: 		      relay, 1 NO contact 230 V / 10 A, 2300 W or 1150 VA (cos ϕ = 0.5)

Switching capacity LED < 2 W:     typ. 40 W

Switching capacity LED > 2 W:     typ. 450 W

Brightness switching value: 	      5 – 3000 lux

Lighting time delay: 		      10 s – 60 min, pulse

Channel H Presence: 		      relay, 1 NO contact, floating, 50 W / 50 VA

Presence switch-on delay: 	      0 s – 10 min

Presence time delay: 		      10 s – 120 min

Protection rating: 		      IP20

Operating temperature: 		      -15 °C to +45 °C

Dimensions: 			      85 x 85 mm, installation depth 37 mm

Installation: 			wall mounting in flush-mounted box size 1

Optional accessories:

Extension of detection area via slave device:

Order No. white: 		2060760 (theMura S180 Slave B UP)

### theSenda B universal remote control

User remote control with integrated lux meter.

Remote control for installers: the free theSenda Plug app is easy to use for commissioning or adjusting the parameters. Parameter sets can be saved and named in a customer-specific way and exported for archiving, for instance via email.

Order no.: 			9070985

### theSenda P service remote control

Order No.: 			9070910

### theSenda S user remote control

Order No.: 			9070911

### Cover theMura FED WH

### White colour, design to match Feller EDIZIOdue

### for details see www.theben.de/theMura

Order No.:			9070786

### Cover theMura LM WH

### White colour, design to match Legrand Mosaic

### for details see www.theben.de/theMura

Order No.:			9070787

### Cover theMura BJBSI WH

### White colour, design to match BJE balance SI

### for details see www.theben.de/theMura

Order No.:			9070788

### Cover theMura JAS WH

### White colour, design to match Jung AS 500

### for details see www.theben.de/theMura

Order No.:			9070789

### Cover theMura MMP WH

### White colour, design to match Merten M-Plan

### for details see www.theben.de/theMura

Order No.:			9070790

### Cover theMura GS WH

### White colour, design to match Gira Standard 55

### for details see www.theben.de/theMura

Order No.:			9070791

### Cover theMura BS WH

### White colour, design to match Berker S.1

### for details see www.theben.de/theMura

Order No.:			9070792

### Cover theMura Theben WH

### White colour, Theben-Design

### for details see www.theben.de/theMura

Order No.:			9070798