# Tender text

# Presence sensor thePassa P360 DALI-2 S UP WH

Order No. white: 		2010390

Features:

- Passive infrared presence sensor DALI-2 for ceiling installation in flush-mounted box

- This device provides information about presence and brightness in the form of a DALI telegram in line with IEC 62386 Part 303/304

- Rectangular detection area 360°, up to 150 m2 (30 m x 5 m)

- Area restriction with cover clips (optional)

- 3 instances for presence – detection area zone 1 + 2 / zone 1 / zone 2

- 2 mixed light measurements

- 3 instances for brightness – detection area zone 1 + 2 / zone 1 / zone 2

- Easy to calibrate brightness measurement

- Test mode for checking function and detection area

- Configurable detection sensitivity

- Can be configured via DALI bus or remote control

- The "theSenda S" or "theSenda B" user remote controls can be used to dim or switch the lamps, to control the blinds, or to execute additional functions via the higher-level control.

- Nice design with exchangeable bezel frames in two colours

- Ceiling installation in flush-mounted box

- Surface-mounted installation possible with surface frame 110A (optional)

- "theSenda B" app remote control (optional) and corresponding "theSenda Plug" app 
(for iOS/Android)

- This device corresponds to EN 60669-2-5 and IEC 62386-101/103/303/304

Technical data:

Operating voltage: 		DALI (in accordance with IEC 62386-101): 10 V – 22.5 V

Power input: 			max. 10 mA

Moving detection area: 	30 m x 4.5 m tangential, 20 m x 4.5 m radial (IH 3 m)

Recommended installation height IH: 	2 – 6 m/max. 15 m

Light measurement: 		approx. 10 – 10,000 lux

Protection rating: 			IP 54 (when installed)

Operating temperature: 		-15 °C to +50 °C

Dimensions: 			Ø 110 mm, installation depth 37 mm

Connection type:			screw terminals / max. 2 x 2.5 mm2

Optional accessories:

### theSenda B universal remote control

User remote control with integrated luxmeter.

Remote control for installers: The free theSenda Plug app (for iOS/Android) is easy to use for commissioning or adjusting the parameters. Parameter sets can be saved and named in a customer-specific way and exported for archiving, for instance via email.

Order No.: 			9070985

### theSenda P service remote control

Order No.: 			9070910

### theSenda S user remote control

Order No.: 			9070911

### Surface frame 110A

Order no. white: 		9070912 (surface frame 110A WH)

Order No. grey: 		9070913 (surface frame 110A GR)

### Bezel frame cover 110 GR

Order No. grey: 			9070591

### Ceiling installation socket 68A

Drill diameter 68 mm

Order No.: 			9070992

### Cover clip for area restriction

5 pieces

Order No.: 			9070921