# Tender text for presence detectors

# Presence detector thePrema S360-101 E UP WH / GR

Passive-infrared presence detector for ceiling installation; automatic presence and brightness-dependent control for lighting and HVAC; square 360° detection area, walking 49 m2 (7 x 7 m), seated 25 m2 (5 x 5 m) at 3 m installation height;

Mixed light measurement suitable for fluorescent lamps (FL/PL/ESL), halogen/incandescent lamps and LEDs;

Operating voltage 110 - 230 V AC / 50 - 60 Hz, energy consumption approx. 0.1 W; Protection rating IP 20, in fitted state IP 40;

Channel A light: relay, 1 NO contact 230 V / 10 A, 2300 W or 1150 VA (cos ϕ = 0.5); can be switched between fully automatic or semi-automatic operation; configurable brightness switching value approx. 5 – 3000 Lux, teach-in function; self-learning time delay 10 s – 60 min; reduction of the time delay when present briefly (short-term presence); connection option for push buttons or switches for manual switching with automatic detection push button/switch; pulse function for staircase light timer switch;

Channel H, presence: relay, 1 NO contact, floating 220 V DC / 50 W or 250 V AC / 50 VA, switch-on delay 0 – 10 min and time delay 10 s – 120 min, room monitoring with selective motion detection, configurable sensitivity;

Ready for operation immediately thanks to factory presets; can be configured remotely with remote control; extremely simple configuration of energy-saving behaviour with the new "eco plus" function; test mode to check function and detection area; extension of detection area by master/slave or master/master switch, flexible allocation of relay operating modes;

Installation depth 40 mm, ceiling installation in flush-mounted box size 1 or ceiling installation socket 73A, ceiling installation possible with back box 110A;

Manufacturer: thebenHTS

Type: thePrema S360-101 E UP..

Order no.: 2070605 (thePrema S360-101 E UP WH, white)

2070606 (thePrema S360-101 E UP GR, grey)

Unit: ST

### Accessories

Extension of detection area via slave device:

Optional

Type: thePrema S360 Slave E UP..

Order no.: 2070630 (thePrema S360 Slave E UP WH, white)

2070631 (thePrema S360 Slave E UP GR, grey)

### Management remote control "SendoPro 868-A"

Optional

For the installer for start-up or adjustment to usage conditions.

Text-based user guidance in the display. Transmission of individual setting values or complete parameter sets to the detector possible. Suitable for all remote controlled thebenHTS presence detectors.

Order no.: 9070675

### Service remote control "theSenda P"

Optional

Order no.: 9070910

### User remote control "theSenda S"

Optional

Order no.: 9070911

### Back box 110A WH

Optional

Order no.: 9070912

### Back box 110A GR

Optional

Order no.: 9070913

### Ceiling installation socket 73A

Optional

Drill diameter 73 mm

Order no.: 9070917