# Tender text for presence detectors

# Presence detector theRonda P360 KNX UP WH / GR

Passive-infrared presence detector for ceiling installation; automatic presence and brightness-dependent control for lighting and HVAC; round 360° detection area, walking up to 452 m2 (Ø 24 m), installation height up to 10 m, range restriction with covering clips (optional);

Mixed light measurement suitable for fluorescent lamps (FL/PL/ESL), halogen/incandescent lamps and LEDs;

Energy consumption approx. 8 mA / 9 mA with LED on; protection rating IP 20, IP 40 when installed; operating temperature -15° C to +50° C;

2 channels for light C1, C2; switched mode or constant light control with stand-by functionality (orientation light); switched mode with dimmable lighting; can be switched as operation as fully or semi-automatic; brightness switching value or setpoint adjustable in lux via parameter, object or remote control; teach-in of brightness switching value or setpoint; reduction of time delay during brief presence (brief presence); manual override by means of telegram or remote control;

2 channels for presence C4, C5, individually programmable; switch-on delay and time delay adjustable;

Separate disable object for light and presence channel; recording and transmitting of the current brightness; configuration of the room correction factor for comparing the brightness measurement; configurable sensitivity; test mode to check function and detection area;scenes; extension of detection area by parallel switching of several motion detectors (master / slave or master / master); can be configured remotely with remote control.

Installation depth 37 mm, ceiling installation in flush-mounted box, size 1 or ceiling installation socket 73A, ceiling installation possible with back box 110 A, Protection rating IP 44;

Manufacturer: 	thebenHTS

Type: 		theRonda P360 KNX UP..

Order no.: 2089000 (theRonda P360 KNX UP WH, white)

2089001 (theRonda P360 KNX UP GR, grey)

Unit: ST

### Accessories

### Management remote control "SendoPro 868-A"

Optional

For the installer for start-up or adjustment to usage conditions.

Text-based user guidance in the display. Transmission of individual setting values or complete parameter sets to the detector possible. Suitable for all remote controlled thebenHTS presence detectors.

Order no.: 9070675

### Service remote control "theSenda P"

Optional

Order no.: 9070910

### User remote control "theSenda S"

Optional

Order no.: 9070911

### Back box 110A WH

Optional

Order no.: 9070912

### Back box 110A GR

Optional

Order no.: 9070913

### Ceiling installation socket 73A

Optional

Drill diameter 73 mm

Order no.: 9070917

### Covering clip for area restriction

Optional

Order no.: 9070921